## Distanciamiento
Elevación solar y Acimut en Málaga, Santander
Longitud [m] |  | L | 2
Inclinación deseada del panel [ ° ] |  | B | 15 | a Radianes | 0.2618
Elevacion del sol [ ° ] |  | A | 30 | a Radianes | 0.5236
|  | Sen ( B ) | 0.25882
|  | Tan ( A ) | 0.57735
|  | Cos ( B ) | 0.96593
| Constante de inclinación | K | 1.4142
| Separación entre strings [ m ] | D | 2.8284
Nota: La grafica muestra la elevación solar media, en el municipio de Málaga, Santander, fuente : https://es.weatherspark.com/h/y/149861/2022/Datos-hist%C3%B3ricos-meteorol%C3%B3gicos-de-2022-en-el-Aeropuerto-Internacional-de-Palonegro-Colombia
Datos ingreados

## Cuadro de Cargas
CARGAS INSTALADAS | [5 empty] | AREA
DESCRIPCIÓN | POTENCIA (W) | CANTIDAD | TOTAL CARGA [W] | Horas de Uso | Energía [Wh/día] | 90
Circuito de pequeños aparatos y herramientas | 500 | 1 | 500 | 5 | 2500 | Estrato
Iluminacion LED 12W | 12 | 4 | 48 | 5 | 240 | 1
Barra de sonido | 40 | 2 | 80 | 6 | 480 | Tensión [V]
Computador Portatil | 250 | 2 | 500 | 4 | 2000 | 120
Motor 1f | 500 | 1 | 500 | 2 | 1000
Potencia Instalada [W] |  |  | 1628
Energia Requerida [Wh/día] |  |  | 6220

## Climatologia
Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14
-BEGIN HEADER-
NASA/POWER CERES/MERRA2 Native Resolution Climatology Climatologies
11-year Meteorological and Solar Monthly & Annual Climatologies (January 2011 - December 2021)
Location: Latitude 6.705 Longitude -72.7332
Elevation from MERRA-2: Average for 0.5 x 0.625 degree lat/lon region = 2898.39 meters
The value for missing source data that cannot be computed or is outside of the sources availability range: -999
Parameter(s):
ALLSKY_KT SRB V4/CERES SYN1deg All Sky Insolation Clearness Index (dimensionless)
ALLSKY_SFC_UVA SRB V4/CERES SYN1deg All Sky Surface UVA Irradiance (W/m^2)
ALLSKY_SFC_UVB SRB V4/CERES SYN1deg All Sky Surface UVB Irradiance (W/m^2)
ALLSKY_SRF_ALB SRB V4/CERES SYN1deg All Sky Surface Albedo (dimensionless)
SG_DAY_COZ_ZEN_AVG SRB V4/CERES SYN1deg Daylight Average Of Hourly Cosine Solar Zenith Angles for Climatological Month (Degrees)
ALLSKY_SFC_UV_INDEX SRB V4/CERES SYN1deg All Sky Surface UV Index (dimensionless)
INSOL_CONSEC_MONTH_MIN SRB V4/CERES SYN1deg Minimum Available Insolation Over A Month Period (kW-hr/m^2/day)
EQUIV_NO_SUN_CONSEC_MONTH SRB V4/CERES SYN1deg Equivalent No-Sun Days Over A Month Period (Days)
SOLAR_DEFICITS_CONSEC_MONTH SRB V4/CERES SYN1deg Solar Irradiance Deficit Over A Month Period (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_HORIZONTAL SRB V4/CERES SYN1deg Solar Irradiance for Equator Facing Horizontal Surface (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_LAT_MINUS15 SRB V4/CERES SYN1deg Solar Irradiance for Equator Facing Latitude Minus 15 Tilt (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_LATITUDE SRB V4/CERES SYN1deg Solar Irradiance for Equator Facing Latitude Tilt (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_LAT_PLUS15 SRB V4/CERES SYN1deg Solar Irradiance for Equator Facing Latitude Plus 15 Tilt (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_VERTICAL SRB V4/CERES SYN1deg Solar Irradiance for Equator Facing Vertical Surface (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_OPTIMAL SRB V4/CERES SYN1deg Solar Irradiance Optimal (kW-hr/m^2/day)
SI_EF_TILTED_SURFACE_OPTIMAL_ANG SRB V4/CERES SYN1deg Solar Irradiance Optimal Angle (Degrees)
SI_EF_TILTED_SURFACE_OPTIMAL_ANG_ORT SRB V4/CERES SYN1deg Solar Irradiance Tilted Surface Orientation (N/S Orientation)
Message(s):
The Battery Sizing parameters are computed for January 2001 to December 2020 not a custom climatological period; the parameters are EQUIV_NO_SUN_CONSEC_MONTH | SOLAR_DEFICITS_CONSEC_MONTH | INSOL_CONSEC_MONTH_MIN
Column1: -END HEADER- | Hora Solar Pico | Angulo | Mes
PARAMETER | JAN | FEB | MAR | APR | MAY | JUN | JUL | AUG | SEP | OCT | NOV | DEC | ANN | 5.48 | 3.29 | JAN | Caso Crítico
ALLSKY_KT | 0.54 | 0.49 | 0.41 | 0.39 | 0.41 | 0.42 | 0.42 | 0.43 | 0.44 | 0.44 | 0.46 | 0.52 | 0.44 | 5.03 | 2.56 | FEB | HSP | Mes
ALLSKY_SFC_UVA | 13.93 | 13.73 | 12.1 | 11.81 | 12.91 | 13.03 | 12.97 | 12.86 | 13.0 | 13.21 | 13.12 | 13.67 | 13.03 | 4.23 | 1.76 | MAR | 3.97 | APR
ALLSKY_SFC_UVB | 0.44 | 0.45 | 0.4 | 0.39 | 0.42 | 0.41 | 0.41 | 0.41 | 0.42 | 0.42 | 0.41 | 0.43 | 0.42 | 3.97 | 1.46 | APR
ALLSKY_SRF_ALB | 0.12 | 0.13 | 0.13 | 0.13 | 0.14 | 0.14 | 0.14 | 0.13 | 0.13 | 0.14 | 0.14 | 0.13 | 0.13 | 4.13 | 1.54 | MAY
SG_DAY_COZ_ZEN_AVG | 0.57 | 0.6 | 0.63 | 0.63 | 0.62 | 0.61 | 0.61 | 0.63 | 0.64 | 0.62 | 0.58 | 0.56 | -999.0 | 4.19 | 1.56 | JUN
ALLSKY_SFC_UV_INDEX | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | -999.0 | 4.24 | 1.56 | JUL
INSOL_CONSEC_MONTH_MIN | 129.82 | 117.47 | 114.94 | 106.86 | 119.43 | 119.39 | 122.95 | 119.32 | 119.92 | 124.93 | 119.79 | 131.2 | -999.0 | 4.32 | 1.54 | AUG
EQUIV_NO_SUN_CONSEC_MONTH | 5.09 | 4.96 | 4.52 | 3.23 | 2.15 | 1.51 | 1.97 | 3.23 | 2.89 | 2.53 | 2.1 | 2.94 | -999.0 | 4.41 | 1.68 | SEP
SOLAR_DEFICITS_CONSEC_MONTH | 25.49 | 25.0 | 19.64 | 12.9 | 8.89 | 6.32 | 8.35 | 13.87 | 12.78 | 11.11 | 9.03 | 13.76 | -999.0 | 4.43 | 2.15 | OCT
SI_EF_TILTED_SURFACE_HORIZONTAL | 4.96 | 4.84 | 4.21 | 3.97 | 4.08 | 4.11 | 4.18 | 4.3 | 4.41 | 4.38 | 4.3 | 4.68 | -999.0 | 4.49 | 2.57 | NOV
SI_EF_TILTED_SURFACE_LAT_MINUS15 | 4.62 | 4.64 | 4.14 | 3.96 | 4.13 | 4.18 | 4.23 | 4.32 | 4.37 | 4.26 | 4.11 | 4.36 | -999.0 | 5.17 | 3.24 | DEC
SI_EF_TILTED_SURFACE_LATITUDE | 5.16 | 4.95 | 4.23 | 3.94 | 4.01 | 4.02 | 4.09 | 4.24 | 4.4 | 4.42 | 4.4 | 4.87 | -999.0
SI_EF_TILTED_SURFACE_LAT_PLUS15 | 5.45 | 5.02 | 4.13 | 3.74 | 3.73 | 3.7 | 3.78 | 3.98 | 4.24 | 4.38 | 4.49 | 5.14 | -999.0
SI_EF_TILTED_SURFACE_VERTICAL | 3.29 | 2.56 | 1.76 | 1.46 | 1.54 | 1.56 | 1.56 | 1.54 | 1.68 | 2.15 | 2.57 | 3.24 | -999.0
SI_EF_TILTED_SURFACE_OPTIMAL | 5.48 | 5.03 | 4.23 | 3.97 | 4.13 | 4.19 | 4.24 | 4.32 | 4.41 | 4.43 | 4.49 | 5.17 | -999.0
SI_EF_TILTED_SURFACE_OPTIMAL_ANG | 26.5 | 17.5 | 3.5 | -8.0 | -13.5 | -16.0 | -17.0 | -10.5 | -1.0 | 8.0 | 17.0 | 26.0 | -999.0
SI_EF_TILTED_SURFACE_OPTIMAL_ANG_ORT | bar: JAN to DEC

## Componentes
Horas Solares Pico (HSP) | Energia Requerida (ER) | Potencia Instalada
3.97 | 6220 | 1628 |  |  |  | CALCULO DE CONDUCTORES Y PROTECCIONES DEL SISTEMA
|  |  | Ah | 200 |  | Voc panel |  | 34.88
Potencia pico [W] | 1566.7506 |  | C | 304.902 |  | Isc panel |  | 11.03
Potencia nominal [W] | 400 |  | Baterias | 1.5245 |  | Vmax |  | 29.26 | tamb | 18 |  |  |  | TOTAL
N° de paneles | 3.9169 |  | VDC baterias | 24 |  | Imax |  | 10.32 | tmax | 30 |  | Voc(30) | 33.729 | 134.9158
[6 empty] | cantidad de paneles |  | 4 | tmin | 10 |  | Isc(30) | 11.0896 | 44.3582
[6 empty] | Factor de seguridad |  | 1.25
Paneles | 4 X 400 |  | Baterias | 2 X 200 Ah |  | Factor corrección por agrupamiento |  | 1.04 | B | -0.00275
[6 empty] | Factor corrección por temperatura |  | 0.7 | A | 0.00045 |  | Voc(10) | 35.6474 | 142.5894
[9 empty] | Y | -0.0035 |  | Isc(10) | 10.9903 | 43.9612
| Potencia [W] | Tensión salida [V] |  |  | Tramo Panel a Barraje DC | Corriente del fusible [A] |  | 13.7875
Inversor al 75% de simultaneidad | 1465.2 | 110 | VAC |  |  | Ajustado al valor comercial [A] |  | 15 | voc | 34.88 | 139.52
Inversor valores comerciales | 1500 |  |  |  |  | Conductor y ampacity | PV XLPE No 10 CU | 29.12 | isc | 11.03 | 44.12
[6 empty] | Termomagnetico DC [A] |  | 13.7875
[6 empty] | Ajustado al valor comercial DC [A] |  | 15
Controlador de carga FV | Valor Nominal del sistema | Ajuste a Valor comercial |  |  | Tramo Barraje DC a Inversor | Corriente del fusible [A] |  | 44.12
Tension [V] | 139.52 | 140 |  |  |  | Ajustado al valor comercial [A] |  | 45
Corriente de carga [A] | 66.6667 | 70 |  |  |  | Conductor y ampacity | PV XLPE No 8 CU | 55
[6 empty] | Termomagnetico DC [A] |  | 44.12
[6 empty] | Ajustado al valor comercial DC [A] |  | 45
[6 empty] | Termomagnetico AC [A] |  | 17.0455
[6 empty] | Ajuste a valor comercial AC [A] |  | 20
[5 empty] | Tramo Panel a Barraje DC | Termomagnetico DC [A] |  | 13.7875
[6 empty] | Ajustado al valor comercial DC [A] |  | 16
[5 empty] | Tramo Barraje DC a Inversor | Termomagnetico DC [A] |  | 44.12
[6 empty] | Ajustado al valor comercial DC [A] |  | 45

## Soportes y tubería
CONDUIT IMC
Tubería
[6 empty] | Diametro Nominal | Diametro interior [mm] | Área [mm]
Conductor: | Calibre | Diametro mm | Área unitaria | No de conductores | Área Total
PV XLPE Cu 600V 90°C | 10 | 7.1 | 39.5919 | 8 | 316.7354 | 1/2" | 16.76 | 220.6165
AWG XLP 90°C Tierra | 8 | 7.8 | 47.7836 | 1 | 47.7836 | 3/4" | 21.95 | 378.4068
[6 empty] | 1" | 28.07 | 618.8348
|  |  |  | Total: | 364.519 | 1-1/4" | 36.78 | 1062.4618
[6 empty] | 1-1/2" | 42.75 | 1435.3642
[6 empty] | 2" | 54.61 | 2342.2553
[6 empty] | 2-1/2" | 64.95 | 3313.2041
[6 empty] | 3" | 80.67 | 5111.0955
Conduit | 1-1/4" |  |  |  |  | 4" | 105.82 | 8794.7884
Área | 1062.4618
% Ocupación | 34 | Cumple

## AeroGenerador
[6 empty] | Velocidad media [km/h] | Potencia del viento por area [W/m2] | Energía del viento por hora [Wh] | Energía del viento por día [Wh/día]
[5 empty] | Enero | 6.3 | 76.5769 | 146.2511 | 3510.0263
| Datos del sitio |  |  |  | Febrero | 6.6 | 88.0456 | 168.1548 | 4035.7153
[5 empty] | Marzo | 6.6 | 88.0456 | 168.1548 | 4035.7153
[5 empty] | Abril | 6.2 | 72.988 | 139.3967 | 3345.5212
Velocidad media del viento [m/s] |  | 2 | km/h |  | Mayo | 6.3 | 76.5769 | 146.2511 | 3510.0263
|  |  | 7.2 |  | Junio | 7.4 | 124.0999 | 237.0133 | 5688.3181
Altura [msnm] |  | 2235 |  |  | Julio | 7.8 | 145.3315 | 277.5628 | 6661.5076
Temperatura media [°C] |  | 16 |  |  | Agosto | 7 | 105.0438 | 200.6188 | 4814.8508
Densidad del aire [kg/m3] |  | 1.225 |  |  | Septiembre | 5.9 | 62.8973 | 120.125 | 2883.0007
Area de barrido [m2] |  | 0.5 |  |  | Octubre | 4.9 | 36.03 | 68.8122 | 1651.4938
[5 empty] | Noviembre | 4.1 | 21.1071 | 40.3115 | 967.4762
[5 empty] | Diciembre | 5.1 | 40.6244 | 77.5868 | 1862.0839
1.7176
E requerida | 6220 | Wh/día |  |  |  | Velocidad del viento [km/h] | Potencia del viento [W/m2] | Energía del viento por hora [Wh] | Energía del viento por día [Wh/día]
Em viento | 3580.478 | Wh/día |  |  | Media | 6.1833 | 78.1139 | 149.1866 | 3580.478
AG en valor comercial | 4000 | Wh/día
V de inicio | 2 | m/s

## GrupoElectrogeno
| P [W] | Factor de arranque | P total [W]
Cargas No motrices | 1128 | 1 | 1128
Cargas motrices | 500 | 3 | 1500
|  | Total | 2628
|  | Total en kW | 2.628
|  | FP | 0.85
|  | Total en kVA | 3.0918
|  | % FS | 20
| Grupo Electrógeno |  | 3.7101 | kVA
| GE en valor comercial |  | 4 | kVA